## Slide 1: Post-earthquake Serviceability Assessment of Water Distribution Networks based on Pressure Dependent Demand Model
Zhao HAN College of Architecture and Civil Engineering
Beijing University of Technology
May 26, 2018

## Slide 2: CONTENTS
01 Post-earthquake serviceability assessment method
02 Resilience of Water Supply Network

## Slide 3: 01 Post-earthquake serviceability assessment method
The Procedure of Assessment Method
Earthquake Damaged Pipe Model
Pressure Driven Demand (PDD) Model

## Slide 4: Procedure of the Assessment Method
step1. Calculate the seismic failure probabilities of pipelines (pf); the RR stands for Repair Rate.
Step2. Generate a uniform distributed random number r∈[0,1]
Step3. Generate the damage locations in the pipeline.
L
A
B
Break node 1
Break node 2
Break node 3
L2
L3
L4
L1

## Slide 5: Procedure of the Assessment Method
step4. Identify the leak type
Step5. Generate the hydraulic model for breaks and leaks
Step6. Hydraulic analysis with epanet2.dll consider the PDD Model

## Slide 6: Procedure of the Assessment Method
Step7. Calculate the serviceability index
  the node serviceability index (SI)
  the system serviceability index (SSI)

## Slide 7: Earthquake Damaged Pipe Hydraulic Model
Pipe break
  The complete separation of a pipeline
  No flow will pass
Pipe leak
  a small leak in a pipeline
  water will continue to flow through the pipeline
  flow being lost through the leak
Virtual Reservoir
Emitter

## Slide 8: Pressure Driven Demand Model
(b)
Negative pressure node
P1
P7
P8
P4
P5
P6
P12
P13
P9
P10
P11
P2
P3
(a)
NO change in the topology of the WDN
The water supply (Qi*) in a node i
Pressure deficient node

## Slide 9: Case Study and Results
The Overview of the WDN
  49 junctions
  78 pipes
  4 reservoirs

## Slide 10: Case Study and Results
CONCLUSIONS:
  The amount of water distributed changes in the same trend as the GIRAFFE
  The convergence performance of the method is better than GIRAFFE

## Slide 11: 02 Resilience of Water Supply Network
Definition
the ability to resist the earthquake hazards, absorb the initial damage, and recover to the normal operation
100%
Functionality(t)
time
t1
t2
t3
t4
90%
Failure path
t0
t5
Recovery path
Initial failure
Resilience Index

## Slide 12: 02 Resilience of Water Supply Network
Some problems:
  The definition of the resilience
  How to definite the functionality of the water supply network ?
  How to describe the recovery procedure of the water supply network after an earthquake?
    The time needed to locate a pipe break.
    The time needed to repair a pipe break.
    cascading damage to interrelated systems

## Slide 13
THE END
THANK YOU VERY MUCH